## Setup
Notes
Settings
Spreadsheet Version | 0.4.2 |  |  |  | Do NOT change this unless advised
User Id | name |  |  |  | This is the tag that is applied to your running instances so that you can identify which instances are yours.
OpenStudio Server Version | 1.12.4 |  |  |  | Choose which OpenStudio Server Version to Use. Do NOT change this unless advised. Note that this is not the OpenStudio version. See mappings here: http://developer.nrel.gov/downloads/buildings/openstudio/rsrc/amis_v2.json
Cluster Name | FDD-LDRD |  |  |  | This is the name used to identify the compute cluster (snake-cased). If you use this name in other spreadsheets, then you are able to submit multiple jobs to the same compute cluster.
Server Instance Type | m3.medium | Use only for cluster configuration testing | 1 Cores with 4 GB | $0.07/hour | Use a minimum of 2 cores for server.
Worker Instance Type | m3.large | Recommended for Server | 2 Cores with 32 GB | $0.14/hour | Depends on how many simuations. If you are testing, then you can select a smaller instance.
Worker Nodes | 1 |  | Total Cost | $0.21/hour | Number of worker nodes to start. This can be zero for testing purposes (all simulations will be run on the server node).
AWS Tag | org=5500 |  |  |  | Add extra tags to your instances (key=value). Add another line if you need another tag.
Running Setup
Analysis Name | SEB_DT_HS |  |  |  | Display name of the analysis
Measure Directory | ../fault_measures |  |  |  | Relative to this spreadsheet or absolute path
Export Directory | ../analysis |  |  |  | Relative to this spreadsheet or absolute path
Allow Multiple Jobs | TRUE |  |  |  | Do NOT change this unless advised
Use Server As Worker | TRUE |  |  |  | Typically leave this as TRUE unless you are running many worker nodes
Simulate Data Point Filename | simulate_data_point.rb |  |  |  | Do NOT change this unless advised
Run Data Point Filename | run_openstudio_workflow_monthly.rb |  |  |  | Do NOT change this unless advised
Problem Definition | Problem Type |  |  |  | Place any Problem Specific entries here. The names will be downcased and underscored automatically, so either enter them as readable or already "snake_cased". Note the values won't be downcased or snake_cased.
Analysis Type | baseline_perturbation
Algorithm Setup | Configuration Values | Allowed Values and Description | Override Defaults (Enter values here to override the Defaults in Column B) |  | Place any Problem Specific entries here. The names will be downcased and underscored automatically, so either enter them as readable or already "snake_cased". Note the values won't be downcased or snake_cased.
in_measure_combinations | TRUE | (TRUE/FALSE) Run full factorial search over in-measure variable combinations
include_baseline_in_combinations | FALSE | (TRUE/FALSE) If in_measure_combinations are TRUE, sets if static values be included in combinations | FALSE
Weather Files | Path (relative to this spreadsheet or absolute path) | Weather files in the .zip format. Can list individually or use a wild card
Weather File | ../weather/SRRL_2012AMY_60min.epw
Models | Identifier | File Type | Path (relative to this spreadsheet or absolute path) |  | If there are more than one seed models, then you will submit the same analysis for each seed model.
Model | SEB_DT_HS | OSM | ../seeds/SEB_160.osm |  | You can change the identifier (which becomes the file name for the zip and json file) and the seed model location.
Other Library Files | Directory to Unpack to | Files to include (relative to this spreadsheet or absolute path). If a directory then it will include all subfolders and files |  |  | If extra library files are needed then include them here. These are typically preprocessors or postprocessors and require custom measures to use.
Worker Initialization Scripts - Name | Path (relative or absolute) to local script | Arguments (in the form of an array ["19837,"z",{b: 'something'}]) |  |  | These scripts will be executed in this order on each worker node when it is initialized. These can be used to download any analysis-wide files such as BCL data, utility data, etc. Name is arbitary, but a name must exist to include the line.
Worker Finalization Scripts - Name | Path (relative or absolute) to local script) | Arguments (in the form of an array ["19837,"z",{b: 'something'}]) |  |  | These scripts will be executed in this order on each worker node when it is finalized. Can be used to push all the results of the anlaysis to a specific location. Name is arbitary, but a name must exist to include the line.

## Variables
|  |  | Inputs | [6 empty] | Continuous Variable Description |  |  |  |  | Discrete Variable Description |  |  |  |  | Other Notes
# Measure Enabled | Measure Display Name | Measure Directory Name | Measure Class Name
# Variable | type | Measure Directory | Parameter Display Name (will make machine name) | Parameter Name in Measure | Parameter Short Display Name | Variable Type | Units | Static/Default Value | Enumerations | Min | Max | Mean | Std Dev | delta_x | Discrete Values | Discrete Weights | Distribution | Data Source | Notes | Typical var to eui relationship | Screening Min | Screening Max | Screening Mean | Screening Std Dev
TRUE | Auto Size to Hard Size E Plus Version | AutoSizeToHardSizeEPlusVersion | AutoSizeToHardSizeEPlusVersion | RubyMeasure
| argument |  | EnergyPlus version in use | eplus_version | EnergyPlus version in use | Double |  | 8.2
TRUE | Add Meter 1 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | Electricity:Facility
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 2 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | InteriorLights:Electricity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 3 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | InteriorEquipment:Electricity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 4 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | Fans:Electricity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 5 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | Pumps:Electricity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 6 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | Heating:Electricity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 7 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | HeatRecovery:Electricity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 8 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | Cooling:Electricity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 9 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | Electricity:Facility
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Meter 10 | AddMeter | AddMeter | RubyMeasure
| argument |  | Enter Meter Name | meter_name |  | String |  | Gas:Facility
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 1 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Site Outdoor Air Drybulb Temperature
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 2 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Site Outdoor Air Relative Humidity
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 3 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Site Wind Speed
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 4 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Zone Air Temperature
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 5 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | variable_name | variable_name |  | String |  | Zone Air Relative Humidity
| argument |  | reporting_frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 6 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | variable_name | variable_name |  | String |  | Air System Outdoor Air Mass Flow Rate
| argument |  | reporting_frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 7 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Air System Mixed Air Mass Flow Rate
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 8 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Chiller Electric Power
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 9 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Boiler Gas Energy
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 10 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | Enter Variable Name | variable_name |  | String |  | Cooling Coil Total Cooling Energy
| argument |  | Reporting Frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 11 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | variable_name | variable_name |  | String |  | Cooling Coil Sensible Cooling Energy
| argument |  | reporting_frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 12 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | variable_name | variable_name |  | String |  | Heating Coil Heating Energy
| argument |  | reporting_frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Add Output Variable 13 | AddOutputVariable | AddOutputVariable | RubyMeasure
| argument |  | variable_name | variable_name |  | String |  | Pump Electric Energy
| argument |  | reporting_frequency | reporting_frequency |  | Choice |  | timestep | ¦detailed,timestep,hourly,daily,monthly¦
TRUE | Output For Evaluation | OutputForEvaluation | OutputForEvaluation | EnergyPlusMeasure
| argument |  | Enter the electricity cost (US$/kWh) | cost_per_kwh |  | Double |  | 0.0986
| argument |  | Enter the gas cost (US$/ccf) | cost_per_ccf |  | Double |  | 7.25
TRUE | Xcel EDA Tariff Selection and Model Setup | XcelEDATariffSelectionandModelSetup | XcelEDATariffSelectionandModelSetup | EnergyPlusMeasure
| argument |  | Select an Electricity Tariff. | elec_tar |  | Choice |  | Secondary General | ¦Residential General,Commercial,Primary General,Secondary General Low Load Factor,Secondary General,Secondary Photovoltaic Time-of-Use,Transmission General,Non-Xcel Commercial,Non-Xcel Primary General,Non-Xcel Secondary General Low Load Factor,Non-Xcel Secondary General,Non-Xcel Transmission General¦
| argument |  | Select a Gas Tariff. | gas_tar |  | Choice |  | Large CG | ¦Residential Gas,Small CG,Large CG,Interruptible Industrial G,Non-Xcel Gas Firm,Non-Xcel Gas Interruptible¦
TRUE | Xcel EDA Reporting and QAQC | XcelEDAReportingandQAQC | XcelEDAReportingandQAQC | ReportingMeasure
TRUE | ExportTimeSeriesDatatoCSV | ExportTimeSeriesDatatoCSV | ExportTimeSeriesDatatoCSV | ReportingMeasure
TRUE | Rtuuc With Shr Change | RTUUCWithSHRChange | RTUUCWithSHRChange | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | String |  | Coil Cooling DX Single Speed 1 | ¦Coil Cooling DX Single Speed 1¦
| variable |  | Percentage reduction of charge level [%] | fault_lvl | Percentage reduction of charge level [%] | Double |  | 0 | ¦0, 30¦ | 0 | 30 | 15 |  |  | [30] | [1] | discrete_uncertain
| argument |  | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | q_rat | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | W | -1
| argument |  | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | shr_rat | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double |  | -1
| argument |  | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | vol_rat | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | m3/s | -1
| argument |  | Minimum value of fault level [%] | min_fl | Minimum value of fault level | Double |  | 30
| argument |  | Coefficient a1 for cooling capacity adjustment | Q_CHa1 |  | Double |  | 7.7179
| argument |  | Coefficient a2 for cooling capacity adjustment | Q_CHa2 |  | Double |  | -10.765
| argument |  | Coefficient a3 for cooling capacity adjustment | Q_CHa3 |  | Double |  | 3.129
| argument |  | Coefficient a4 for cooling capacity adjustment | Q_CHa4 |  | Double |  | -0.88403
| argument |  | Coefficient a5 for cooling capacity adjustment | Q_CHa5 |  | Double |  | 0.30043
| argument |  | Coefficient a6 for cooling capacity adjustment | Q_CHa6 |  | Double |  | -0.036993
| argument |  | Coefficient a1 for EIR adjustment | EIR_CHa1 |  | Double |  | -5.7419
| argument |  | Coefficient a2 for EIR adjustment | EIR_CHa2 |  | Double |  | 8.6709
| argument |  | Coefficient a3 for EIR adjustment | EIR_CHa3 |  | Double |  | -4.4104
| argument |  | Coefficient a4 for EIR adjustment | EIR_CHa4 |  | Double |  | 1.2489
| argument |  | Coefficient a5 for EIR adjustment | EIR_CHa5 |  | Double |  | 1.2095
| argument |  | Coefficient a6 for EIR adjustment | EIR_CHa6 |  | Double |  | 0.36051
| argument |  | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | min_wb_tmp_uc | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 12.8
| argument |  | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | max_wb_tmp_uc | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 23.9
| argument |  | Minimum value of condenser air inlet temperature for the non-condensable model | min_cond_tmp_uc | Minimum value of condenser air inlet temperature for the non-condensable model | Double |  | 18.3
| argument |  | Maximum value of condenser air inlet temperature for the non-condensable model | max_cond_tmp_uc | Maximum value of condenser air inlet temperature for the non-condensable model | Double |  | 46.1
| argument |  | Minimum value of rated COP for the non-condensable model | min_cop_uc | Minimum value of rated COP for the non-condensable model | Double |  | 3.74
| argument |  | Maximum value of rated COP for the non-condensable model | max_cop_uc | Maximum value of rated COP for the non-condensable model | Double |  | 4.69
| argument |  | Percentage change of UA with increase of charge level | bf_para | Percentage change of UA with increase of charge level | Double | % of BF/% of charge level | -1.39
TRUE | Rtuca With Shr Change | RTUCAWithSHRChange | RTUCAWithSHRChange | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | String |  | Coil Cooling DX Single Speed 1
| variable |  | Percentage reduction of condenser airflow [%] | fault_lvl | Percentage reduction of condenser airflow [%] | Double |  | 0 | ¦0, 50¦ | 0 | 50 | 15 |  |  | [50] | [1] | discrete_uncertain
| argument |  | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | q_rat | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | W | -1
| argument |  | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | shr_rat | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double |  | -1
| argument |  | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | vol_rat | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | m3/s | -1
| argument |  | Maximum value of fault level | min_fl | Maximum value of fault level | Double |  | 50
| argument |  | Coefficient a1 for cooling capacity adjustment | Q_CAa1 |  | Double |  | -2.2162
| argument |  | Coefficient a2 for cooling capacity adjustment | Q_CAa2 |  | Double |  | 5.6315
| argument |  | Coefficient a3 for cooling capacity adjustment | Q_CAa3 |  | Double |  | -3.1199
| argument |  | Coefficient a4 for cooling capacity adjustment | Q_CAa4 |  | Double |  | 0.22492
| argument |  | Coefficient a5 for cooling capacity adjustment | Q_CAa5 |  | Double |  | -0.76245
| argument |  | Coefficient a6 for cooling capacity adjustment | Q_CAa6 |  | Double |  | -0.072843
| argument |  | Coefficient a1 for EIR adjustment | EIR_CAa1 |  | Double |  | -5.9806
| argument |  | Coefficient a2 for EIR adjustment | EIR_CAa2 |  | Double |  | 0.9479
| argument |  | Coefficient a3 for EIR adjustment | EIR_CAa3 |  | Double |  | 4.3816
| argument |  | Coefficient a4 for EIR adjustment | EIR_CAa4 |  | Double |  | -1.0667
| argument |  | Coefficient a5 for EIR adjustment | EIR_CAa5 |  | Double |  | 2.9142
| argument |  | Coefficient a6 for EIR adjustment | EIR_CAa6 |  | Double |  | 0.090476
| argument |  | Minimum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | min_wb_tmp_uc | Minimum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | Double |  | 12.8
| argument |  | Maximum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | max_wb_tmp_uc | Maximum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | Double |  | 23.9
| argument |  | Minimum value of condenser air inlet temperature for the liquid line restriction model | min_cond_tmp_uc | Minimum value of condenser air inlet temperature for the liquid line restriction model | Double |  | 18.3
| argument |  | Maximum value of condenser air inlet temperature for the liquid line restriction model | max_cond_tmp_uc | Maximum value of condenser air inlet temperature for the liquid line restriction model | Double |  | 46.1
| argument |  | Minimum value of rated COP for the liquid line restriction model | min_cop_uc | Minimum value of rated COP for the liquid line restriction model | Double |  | 3.74
| argument |  | Maximum value of rated COP for the liquid line restriction model | max_cop_uc | Maximum value of rated COP for the liquid line restriction model | Double |  | 4.69
| argument |  | Percentage change of UA with increase of charge level | bf_para | Percentage change of UA with increase of charge level | Double | % of BF/% of charge level | 0
TRUE | Rtull With Shr Change | RTULLWithSHRChange | RTULLWithSHRChange | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | String |  | Coil Cooling DX Single Speed 1
| variable |  | Percentage of liquid line restriction fault [%] | fault_lvl | Liquid line restriction level of the Cooling:Coil:DX:SingleSpeed object | Double |  | 0 | ¦0, 30¦ | 0 | 30 | 15 |  |  | [30] | [1] | discrete_uncertain
| argument |  | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | q_rat | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | W | -1
| argument |  | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | shr_rat | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double |  | -1
| argument |  | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | vol_rat | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | m3/s | -1
| argument |  | Maximum value of fault level | min_fl | Maximum value of fault level | Double |  | 25
| argument |  | Coefficient a1 for cooling capacity adjustment | Q_LLa1 |  | Double |  | -1.0205
| argument |  | Coefficient a2 for cooling capacity adjustment | Q_LLa2 |  | Double |  | -3.2899
| argument |  | Coefficient a3 for cooling capacity adjustment | Q_LLa3 |  | Double |  | 3.66
| argument |  | Coefficient a4 for cooling capacity adjustment | Q_LLa4 |  | Double |  | -1.9118
| argument |  | Coefficient a5 for cooling capacity adjustment | Q_LLa5 |  | Double |  | 0.031398
| argument |  | Coefficient a5 for cooling capacity adjustment | Q_LLa6 |  | Double |  | 0.064409
| argument |  | Coefficient a1 for EIR adjustment | EIR_LLa1 |  | Double |  | 1.4031
| argument |  | Coefficient a2 for EIR adjustment | EIR_LLa2 |  | Double |  | 3.7922
| argument |  | Coefficient a3 for EIR adjustment | EIR_LLa3 |  | Double |  | -5.343
| argument |  | Coefficient a4 for EIR adjustment | EIR_LLa4 |  | Double |  | 3.0229
| argument |  | Coefficient a5 for EIR adjustment | EIR_LLa5 |  | Double |  | 1.6979
| argument |  | Coefficient a5 for EIR adjustment | EIR_LLa6 |  | Double |  | 0.12159
| argument |  | Minimum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | min_wb_tmp_uc | Minimum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | Double |  | 12.8
| argument |  | Maximum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | max_wb_tmp_uc | Maximum value of evaporator air inlet wet-bulb temperature for the liquid line restriction model | Double |  | 23.9
| argument |  | Minimum value of condenser air inlet temperature for the liquid line restriction model | min_cond_tmp_uc | Minimum value of condenser air inlet temperature for the liquid line restriction model | Double |  | 18.3
| argument |  | Maximum value of condenser air inlet temperature for the liquid line restriction model | max_cond_tmp_uc | Maximum value of condenser air inlet temperature for the liquid line restriction model | Double |  | 46.1
| argument |  | Minimum value of rated COP for the liquid line restriction model | min_cop_uc | Minimum value of rated COP for the liquid line restriction model | Double |  | 3.74
| argument |  | Maximum value of rated COP for the liquid line restriction model | max_cop_uc | Maximum value of rated COP for the liquid line restriction model | Double |  | 4.69
| argument |  | Percentage change of UA with increase of charge level | bf_para | Percentage change of UA with increase of charge level | Double | % of BF/% of charge level | -1.32
TRUE | Rtunc With Shr Change | RTUNCWithSHRChange | RTUNCWithSHRChange | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | String |  | Coil Cooling DX Single Speed 1
| variable |  | Non-condensable level of the Cooling:Coil:DX:SingleSpeed object [%] | fault_lvl | Non-condensable level of the Cooling:Coil:DX:SingleSpeed object | Double |  | 0 | ¦0, 60¦ | 0 | 60 | 15 |  |  | [60] | [1] | discrete_uncertain
| argument |  | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | q_rat | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | W | -1
| argument |  | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | shr_rat | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double |  | -1
| argument |  | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | vol_rat | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | m3/s | -1
| argument |  | Minimum value of fault level [%] | min_fl | Minimum value of fault level | Double |  | 80
| argument |  | Coefficient a1 for cooling capacity adjustment | Q_NCa1 |  | Double |  | -1.952
| argument |  | Coefficient a2 for cooling capacity adjustment | Q_NCa2 |  | Double |  | 3.8946
| argument |  | Coefficient a3 for cooling capacity adjustment | Q_NCa3 |  | Double |  | -1.6685
| argument |  | Coefficient a4 for cooling capacity adjustment | Q_NCa4 |  | Double |  | -0.044405
| argument |  | Coefficient a5 for cooling capacity adjustment | Q_NCa5 |  | Double |  | -0.015189
| argument |  | Coefficient a6 for cooling capacity adjustment | Q_NCa6 |  | Double |  | -0.062296
| argument |  | Coefficient a1 for EIR adjustment | EIR_NCa1 |  | Double |  | 2.4648
| argument |  | Coefficient a2 for EIR adjustment | EIR_NCa2 |  | Double |  | -3.1898
| argument |  | Coefficient a3 for EIR adjustment | EIR_NCa3 |  | Double |  | 1.0582
| argument |  | Coefficient a4 for EIR adjustment | EIR_NCa4 |  | Double |  | 0.040316
| argument |  | Coefficient a5 for EIR adjustment | EIR_NCa5 |  | Double |  | -0.000329
| argument |  | Coefficient a6 for EIR adjustment | EIR_NCa6 |  | Double |  | -0.038164
| argument |  | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | min_wb_tmp_uc | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 12.8
| argument |  | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | max_wb_tmp_uc | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 23.9
| argument |  | Minimum value of condenser air inlet temperature for the non-condensable model | min_cond_tmp_uc | Minimum value of condenser air inlet temperature for the non-condensable model | Double |  | 18.3
| argument |  | Maximum value of condenser air inlet temperature for the non-condensable model | max_cond_tmp_uc | Maximum value of condenser air inlet temperature for the non-condensable model | Double |  | 46.1
| argument |  | Minimum value of rated COP for the non-condensable model | min_cop_uc | Minimum value of rated COP for the non-condensable model | Double |  | 3.74
| argument |  | Maximum value of rated COP for the non-condensable model | max_cop_uc | Maximum value of rated COP for the non-condensable model | Double |  | 4.69
| argument |  | Percentage change of UA with increase of charge level | bf_para | Percentage change of UA with increase of charge level | Double | % of BF/% of charge level | 0.373
TRUE | Rtu Condenser Fan Motor Efficiency Fault | RTUCondenserFanMotorEfficiencyFault | RTUCondenserFanMotorEfficiencyFault | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | String |  | Coil Cooling DX Single Speed 1 | ¦Coil Cooling DX Single Speed 1¦
| argument |  | Enter the name of the schedule of the fault levelIf you do not have a schedule, leave this blank | sch_choice | Enter the name of the schedule of the fault levelIf you do not have a schedule, leave this blank | String
| variable |  | Fan motor efficiency degradation level of the Cooling:Coil:DX:SingleSpeed object | degrd_lvl | Fan motor efficiency degradation level of the Cooling:Coil:DX:SingleSpeed object | Double |  | 0 | ¦0, 0.3¦ | 0 | 0.3 | 0.15 |  |  | [0.3] | [1] | discrete_uncertain
| argument |  | Ratio of condenser fan motor power consumption to combined power consumption of condenser fan and compressor at rated condition | fan_power_ratio | Ratio of condenser fan motor power consumption to combined power consumption of condenser fan and compressor at rated condition | Double |  | 0.091747
TRUE | Split Uc With Shr Change | SplitUCWithSHRChange | SplitUCWithSHRChange | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | String |  | Coil Cooling DX Single Speed 1 | ¦Coil Cooling DX Single Speed 1¦
| variable |  | Split Percentage reduction of charge level [%] | fault_lvl | Percentage reduction of charge level [%] | Double |  | 0 | ¦0, 30¦ | 0 | 30 | 15 |  |  | [30] | [1] | discrete_uncertain
| argument |  | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | q_rat | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | W | -1
| argument |  | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | shr_rat | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double |  | -1
| argument |  | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | vol_rat | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | m3/s | -1
| argument |  | Minimum value of fault level [%] | min_fl | Minimum value of fault level | Double |  | 30
| argument |  | Coefficient a1 for cooling capacity adjustment | Q_CHa1 |  | Double |  | -1.6119
| argument |  | Coefficient a2 for cooling capacity adjustment | Q_CHa2 |  | Double |  | -1.9681
| argument |  | Coefficient a3 for cooling capacity adjustment | Q_CHa3 |  | Double |  | 2.5514
| argument |  | Coefficient a4 for cooling capacity adjustment | Q_CHa4 |  | Double |  | -0.98803
| argument |  | Coefficient a5 for cooling capacity adjustment | Q_CHa5 |  | Double |  | 0.34675
| argument |  | Coefficient a6 for cooling capacity adjustment | Q_CHa6 |  | Double |  | 0.10109
| argument |  | Coefficient a1 for EIR adjustment | EIR_CHa1 |  | Double |  | 7.0958
| argument |  | Coefficient a2 for EIR adjustment | EIR_CHa2 |  | Double |  | -1.0132
| argument |  | Coefficient a3 for EIR adjustment | EIR_CHa3 |  | Double |  | -4.9319
| argument |  | Coefficient a4 for EIR adjustment | EIR_CHa4 |  | Double |  | 0.69788
| argument |  | Coefficient a5 for EIR adjustment | EIR_CHa5 |  | Double |  | 1.2677
| argument |  | Coefficient a6 for EIR adjustment | EIR_CHa6 |  | Double |  | -0.065184
| argument |  | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | min_wb_tmp_uc | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 12.8
| argument |  | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | max_wb_tmp_uc | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 23.9
| argument |  | Minimum value of condenser air inlet temperature for the non-condensable model | min_cond_tmp_uc | Minimum value of condenser air inlet temperature for the non-condensable model | Double |  | 18.3
| argument |  | Maximum value of condenser air inlet temperature for the non-condensable model | max_cond_tmp_uc | Maximum value of condenser air inlet temperature for the non-condensable model | Double |  | 46.1
| argument |  | Minimum value of rated COP for the non-condensable model | min_cop_uc | Minimum value of rated COP for the non-condensable model | Double |  | 3.74
| argument |  | Maximum value of rated COP for the non-condensable model | max_cop_uc | Maximum value of rated COP for the non-condensable model | Double |  | 4.69
| argument |  | Percentage change of UA with increase of charge level | bf_para | Percentage change of UA with increase of charge level | Double | % of BF/% of charge level | -1.29
TRUE | Split System Ca With Shr Change | SplitCAWithSHRChange | SplitCAWithSHRChange | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | String |  | Coil Cooling DX Single Speed 1 | ¦Coil Cooling DX Single Speed 1¦
| variable |  | Split Percentage reduction of condenser airflow [%] | fault_lvl | Percentage reduction of condenser airflow [%] | Double |  | 0 | ¦0, 50¦ | 0 | 50 | 15 |  |  | [50] | [1] | discrete_uncertain
| argument |  | Minimum value of fault level | min_fl | Minimum value of fault level | Double |  | 0.5
| argument |  | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | q_rat | Rated cooling capacity of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | W | -1
| argument |  | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | shr_rat | Rated sensible heat ratio of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double |  | -1
| argument |  | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | vol_rat | Rated air flow rate of the cooling coil for bypass factor model adjustmentIf your system is autosized or you do not know what this is, please run the OS Measure Auto Size to Hard Size before this MeasureIf your system is hard sized, leave this value at -1 | Double | m3/s | -1
| argument |  | Minimum value of fault level [%] | min_fl | Minimum value of fault level | Double |  | 50
| argument |  | Coefficient a1 for cooling capacity adjustment | Q_CAa1 |  | Double |  | 1.3037
| argument |  | Coefficient a2 for cooling capacity adjustment | Q_CAa2 |  | Double |  | -0.76356
| argument |  | Coefficient a3 for cooling capacity adjustment | Q_CAa3 |  | Double |  | -0.61117
| argument |  | Coefficient a4 for cooling capacity adjustment | Q_CAa4 |  | Double |  | -0.013457
| argument |  | Coefficient a5 for cooling capacity adjustment | Q_CAa5 |  | Double |  | -0.26911
| argument |  | Coefficient a6 for cooling capacity adjustment | Q_CAa6 |  | Double |  | 0.020726
| argument |  | Coefficient a1 for EIR adjustment | EIR_CAa1 |  | Double |  | -4.5864
| argument |  | Coefficient a2 for EIR adjustment | EIR_CAa2 |  | Double |  | 5.7081
| argument |  | Coefficient a3 for EIR adjustment | EIR_CAa3 |  | Double |  | -1.5167
| argument |  | Coefficient a4 for EIR adjustment | EIR_CAa4 |  | Double |  | -0.13863
| argument |  | Coefficient a5 for EIR adjustment | EIR_CAa5 |  | Double |  | 1.2189
| argument |  | Coefficient a6 for EIR adjustment | EIR_CAa6 |  | Double |  | 0.070849
| argument |  | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | min_wb_tmp_uc | Minimum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 12.8
| argument |  | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | max_wb_tmp_uc | Maximum value of evaporator air inlet wet-bulb temperature for the non-condensable model | Double |  | 23.9
| argument |  | Minimum value of condenser air inlet temperature for the non-condensable model | min_cond_tmp_uc | Minimum value of condenser air inlet temperature for the non-condensable model | Double |  | 18.3
| argument |  | Maximum value of condenser air inlet temperature for the non-condensable model | max_cond_tmp_uc | Maximum value of condenser air inlet temperature for the non-condensable model | Double |  | 46.1
| argument |  | Minimum value of rated COP for the non-condensable model | min_cop_uc | Minimum value of rated COP for the non-condensable model | Double |  | 3.74
| argument |  | Maximum value of rated COP for the non-condensable model | max_cop_uc | Maximum value of rated COP for the non-condensable model | Double |  | 4.69
| argument |  | Percentage change of UA with increase of charge level | bf_para | Percentage change of UA with increase of charge level | Double | % of BF/% of charge level | 0
TRUE | SplitCondenserFanMotorEfficiencyFault | SplitCondenserFanMotorEfficiencyFault | SplitCondenserFanMotorEfficiencyFault | EnergyPlusMeasure
| argument |  | Enter the name of the faulted Coil:Cooling:DX:SingleSpeed object | coil_choice |  | String |  | Coil Cooling DX Single Speed 1
| argument |  | Enter the name of the schedule of the fault level. If you do not have a schedule, leave this blank. | sch_choice |  | String
| variable |  | Split Condenser fan motor efficiency degradation level | degrd_lvl |  | Double |  | 0 | ¦0, 0.3¦ | 0 | 0.3 | 0.15 |  |  | [0.3] | [1] | discrete_uncertain
| argument |  | Ratio of condenser fan power to total condenser fan and compressor power consumption | fan_power_ratio |  | Double |  | 0.052672
TRUE | Heating Thermostat Setpoint Occ Red by Outdoor Temp | HeatingThermostatSetpointOccRedByOutdoorTemp | HeatingThermostatSetpointOccRedByOutdoorTemp | EnergyPlusMeasure
| argument |  | Enter the name of the zone | zone_choice | Enter the name of the zone | String |  | Single zone | ¦Single zone¦
| argument |  | Enter the maximum outdoor air temperature | min_oa_tmp | Enter the maximum outdoor air temperature | Double | C | 5
| variable |  | Enter the expected occupant offset to the heating thermostat | offset_lvl | Enter the expected occupant offset to the thermostat | Double | C | 0 | ¦0, 4¦ | 0 | 4 | 0.15 |  |  | [4] | [1] | discrete_uncertain
TRUE | Cooling Thermostat Setpoint Occ Red by Outdoor Temp | CoolingThermostatSetpointOccRedByOutdoorTemp | CoolingThermostatSetpointOccRedByOutdoorTemp | EnergyPlusMeasure
| argument |  | Enter the name of the zone | zone_choice | Enter the name of the zone | String |  | Single zone | ¦Single zone¦
| argument |  | Enter the minimum outdoor air temperature | min_oa_tmp | Enter the minimum outdoor air temperature | Double | C | 30
| variable |  | Enter the expected occupant offset to the cooling thermostat | offset_lvl | Enter the expected occupant offset to the thermostat | Double | C | 0 | ¦0, 4¦ | 0 | 4 | 0.15 |  |  | [4] | [1] | discrete_uncertain

## Outputs
Outputs
Variable Display Name | Short Display Name | Taxonomy Identifier | Name | Units | Variable Type | Visualize | Export | Objective Function | Objective Function Target | Scale | Objective Function Group
Display Name for Reports | Short display names are used for plots and exported to metadata | Machine Name thats Link to Dencity Taxonomy | Measure/Variable Unique Name |  | double, integer, bool | true/false | true/false | true/false | double | double | integer
Total Natural Gas Intensity | NG EUI | total_natural_gas_intensity | standard_report_legacy.total_natural_gas | MJ/m2 | Double | TRUE | TRUE | TRUE | 140
Total Electricity Intensity | Elec EUI | total_electricity_intensity | standard_report_legacy.total_electricity | MJ/m2 | Double | TRUE | TRUE | TRUE | 590 | 5
Unmet Cooling Hours | NG EUI | total_natural_gas_intensity | standard_reports.time_setpoint_not_met_during_occupied_cooling | hrs | Double | FALSE | TRUE | FALSE
Unmet Heating Hours | Elec EUI | total_electricity_intensity | standard_reports.time_setpoint_not_met_during_occupied_heating | hrs | Double | FALSE | TRUE | FALSE
Total Unmet Hours |  |  | standard_reports.time_setpoint_not_met_during_occupied_hours | hrs | Double | FALSE | TRUE | FALSE
Building Area |  |  | standard_reports.total_building_area | m2 | Double | FALSE | TRUE | FALSE
Natural Gas Heating Intensity |  |  | standard_report_legacy.heating_natural_gas | MJ/m2 | Double | FALSE | TRUE | FALSE
Cooling Electricity Intensity |  |  | standard_report_legacy.cooling_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Interior Lighting Electricity Intensity |  |  | standard_report_legacy.interior_lighting_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Exterior Lighting Electricity Intensity |  |  | standard_report_legacy.exterior_lighting_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Equipment Electricity Intensity |  |  | standard_report_legacy.interior_equipment_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Equipment Natural Gas Intensity |  |  | standard_report_legacy.interior_equipment_natural_gas | MJ/m2 | Double | FALSE | TRUE | FALSE
Experior Equipment Electricity Intensity |  |  | standard_report_legacy.exterior_equipment_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Fans Electricity Intensity |  |  | standard_report_legacy.fans_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Pumps Electricity Intensity |  |  | standard_report_legacy.pumps_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Heat Rejection Electricity Intensity |  |  | standard_report_legacy.heat_rejection_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Humidification Electricity Intensity |  |  | standard_report_legacy.humidification_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Water Systems Electricity Intensity |  |  | standard_report_legacy.water_systems_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Water Systems Natural Gas Intensity |  |  | standard_report_legacy.water_systems_natural_gas | MJ/m2 | Double | FALSE | TRUE | FALSE
Refrigeration Electricity Intensity |  |  | standard_report_legacy.refrigeration_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Total Life Cycle Cost |  |  | standard_report.total_life_cycle_cost | $ | Double | FALSE | TRUE | FALSE
electricity_cost |  |  | xcel_eda_reporting_and_qaqc.electricity_cost | $ | Double | TRUE | TRUE | FALSE
gas_cost |  |  | xcel_eda_reporting_and_qaqc.gas_cost | $ | Double | TRUE | TRUE | FALSE

## BCL Measure Data
FALSE | Add Cost per Area to Construction | AddCostPerAreaToConstruction | RubyMeasure
| argument | Choose a Construction to Add Costs to. | construction | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Area to Unused Construction | AddCostPerAreaToUnusedConstruction | RubyMeasure
| argument | Choose a Construction to Add Costs to. | construction | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Building | AddCostPerFloorAreaToBuilding | RubyMeasure
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Name for Life Cycle Cost Object. | lcc_name | static | String | Building - Life Cycle Costs
| argument | Material and Installation Costs for the Building per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for the Builiding per Floor Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Electric Equipment | AddCostPerFloorAreaToElectricEquipment | RubyMeasure
| argument | Choose a Watts per Area Electric Equipment Definition to Add Costs to. | equip_def | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Definition per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Definition per Floor Area ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Definition per Floor Area ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Lights | AddCostPerFloorAreaToLights | RubyMeasure
| argument | Choose a Watt per Area Lights Definition to Add Costs to. | lights_def | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Definition per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Definition per Floor Area ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Definition per Floor Area ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Unused Lights | AddCostPerFloorAreaToUnusedLights | RubyMeasure
| argument | Choose a Watt per Area Lights Definition to Add Costs to. | lights_def | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Definition per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Definition per Floor Area ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Definition per Floor Area ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost To Supply Side HVAC Component by Air Loop | AddCostToSupplySideHVACComponentByAirLoop | RubyMeasure
| argument | Select an HVAC Air Loop Supply Side Component Type. | hvac_comp_type | static | Choice
| argument | Choose an Air Loop to Add Costs to. | object | static | Choice | **All Air Loops** | ¦**All Air Loops**¦
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs per Component ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Component ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Component ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Daylight Sensor at Center of Spaces with a Specified Space Type Assigned | AddDaylightSensors | RubyMeasure
| argument | Add Daylight Sensors to Spaces of This Space Type | space_type | static | Choice
| argument | Daylighting Setpoint (fc) | setpoint | static | Double | 45
| argument | Daylighting Control Type | control_type | static | Choice | Continuous/Off | ¦None,Continuous,Stepped,Continuous/Off¦
| argument | Daylighting Minimum Input Power Fraction(min = 0 max = 0.6) | min_power_fraction | static | Double | 0.3
| argument | Daylighting Minimum Light Output Fraction (min = 0 max = 0.6) | min_light_fraction | static | Double | 0.2
| argument | Sensor Height (inches) | height | static | Double | 30
| argument | Material and Installation Costs per Space for Daylight Sensor ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Space for Daylight Sensor ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Space for Daylight Sensor ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Exterior Lights | AddExteriorLights | RubyMeasure
| argument | Exterior Lighting Design Power (W) | ext_lighting_level | static | Double | 1000
| argument | End-Use SubCategory | end_use_subcategory | static | String | Exterior Facade Lighting
| argument | Remove Existing Exterior Lights in the Project? | remove_existing_ext_lights | static | Bool | FALSE
| argument | Material and Installation Costs for Exterior Lights ($). | material_cost | static | Double | 0
| argument | Demolition Costs for Exterior Lights ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Exterior Lights ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Output Diagnostics | AddOutputDiagnostics | EnergyPlusMeasure
| argument | Ouput Diagnostic Value. | outputDiagnostic | static | Choice | DisplayExtraWarnings | ¦DisplayAllWarnings,DisplayExtraWarnings,DisplayUnusedSchedules,DisplayUnusedObjects,DisplayAdvancedReportVariables,DisplayZoneAirHeatBalanceOffBalance,DoNotMirrorDetachedShading,DisplayWeatherMissingDataWarnings,ReportDuringWarmup,ReportDetailedWarmupConvergence¦
FALSE | Add Output Variable | AddOutputVariable | RubyMeasure
| argument | Enter Variable Name. | variable_name | static | String
| argument | Reporting Frequency. | reporting_frequency | static | Choice | hourly | ¦detailed,timestep,hourly,daily,monthly¦
FALSE | Add Overhangs by Projection Factor | AddOverhangsByProjectionFactor | RubyMeasure
| argument | Projection Factor (overhang depth / window height) | projection_factor | static | Double | 0.5
| argument | Cardinal Direction | facade | static | Choice | South | ¦North,East,South,West¦
| argument | Remove Existing Space Shading Surfaces From the Model? | remove_ext_space_shading | static | Bool | FALSE
| argument | Optionally Choose a Construction for the Overhangs. | construction | static | Choice
FALSE | Add Simple PV to Shading Surfaces By Type | AddSimplePvToShadingSurfacesByType | EnergyPlusMeasure
| argument | Choose the Type of Shading Surfaces to add PV to | shading_type | static | Choice | Building Shading | ¦Site Shading,Building Shading,Space/Zone Shading¦
| argument | Fraction of Included Surface Area with PV | fraction_surfacearea_with_pv | static | Double | 0.5
| argument | Fractional Value for Cell Efficiency | value_for_cell_efficiency | static | Double | 0.12
| argument | Material and Installation Costs for the PV ($). | material_cost | static | Double | 0
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for the PV ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Adjust Thermostat Setpoints by Degrees | AdjustTheromstatSetpointsByDegrees | RubyMeasure
| argument | Degrees Fahrenheit to Adjust Cooling Setpoint By. | cooling_adjustment | static | Double | 1
| argument | Degrees Fahrenheit to Adjust heating Setpoint By. | heating_adjustment | static | Double | -1
| argument | Alter Design Day Thermostats? | alter_design_days | static | Bool | FALSE
FALSE | Bar Aspect Ratio Study | BarAspectRatioStudy | RubyMeasure
| argument | Total Building Floor Area (ft^2). | total_bldg_area_ip | static | Double | 10000
| argument | Ratio of North/South Facade Length Relative to East/West Facade Length. | ns_to_ew_ratio | static | Double | 2
| argument | Number of Floors. | num_floors | static | Integer | 2
| argument | Floor to Floor Height (ft). | floor_to_floor_height_ip | static | Double | 10
| argument | Surface Matching? | surface_matching | static | Bool | TRUE
| argument | Make Thermal Zones from Spaces? | make_zones | static | Bool | TRUE
FALSE | Enable Demand Controlled Ventilation | EnableDemandControlledVentilation | RubyMeasure
| argument | Choose an Air Loop to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Remove Baseline Costs From Effected AirLoopHVACOutdoorAirSystems? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Air Loop to Enable Demand Controlled Ventilation ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Air Loop to Enable Demand Controlled Ventilation ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Air Loop for Demand Controlled Ventilation ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Enable Economizer Control | EnableEconomizerControl | RubyMeasure
| argument | Choose an Air Loop to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Economizer Control Type. | economizer_type | static | Choice
| argument | Economizer Maximum Limit Dry-Bulb Temperature (F). | econoMaxDryBulbTemp | static | Double | 69
| argument | Economizer Maximum Enthalpy (Btu/lb). | econoMaxEnthalpy | static | Double | 28
| argument | Economizer Maximum Limit Dewpoint Temperature (F). | econoMaxDewpointTemp | static | Double | 55
| argument | Economizer Minimum Limit Dry-Bulb Temperature (F). | econoMinDryBulbTemp | static | Double | -148
| argument | Remove Baseline Costs From Effected AirLoopHVACOutdoorAirSystems? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Air Loop to Enable Economizer ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Air Loop to Enable Economizer ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Air Loop for Economizer ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Export Schedule CSV | ExportScheduleCSV | ReportingMeasure
| argument | Time Interval (minutes) | interval | static | Integer | 60
FALSE | Find and Replace Object Names in the Model | FindAndReplaceObjectNames | RubyMeasure
| argument | Type the text you want search for in object names | orig_string | static | String | replace this text
| argument | Type the text you want to add in place of the found text | new_string | static | String | with this text
FALSE | Improve Fan Belt Efficiency | ImproveFanBeltEfficiency | RubyMeasure
| argument | Choose an Air Loop to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Motor Efficiency Improvement Due to Fan Belt Improvements(%). | motor_eff | static | Double | 3
| argument | Remove Baseline Costs From Effected Fans? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Motor ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Motor ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Motor ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Improve Motor Efficiency | ImproveMotorEfficiency | RubyMeasure
| argument | Choose a Plant or Air Loop to Alter. | object | static | Choice | *All Plant and Air Loops* | ¦*All Plant and Air Loops*¦
| argument | Set Motor Efficiency(%). | motor_eff | static | Double | 96
| argument | Remove Baseline Costs From Effected Fans and Pumps? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Motor ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Motor ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Motor ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set R-value of Insulation for Exterior Walls to a Specific Value | IncreaseInsulationRValueForExteriorWalls | RubyMeasure
| argument | Insulation R-value (ft^2*h*R/Btu). | r_value | static | Double | 13
| argument | Increase in Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_increase_ip | static | Double | 0
| argument | One Time Retrofit Cost to Add Insulation to Construction ($/ft^2). | one_time_retrofit_cost_ip | static | Double | 0
| argument | Year to Incur One Time Retrofit Cost (whole years). | years_until_retrofit_cost | static | Integer | 0
FALSE | Set R-value of Insulation for Roofs to a Specific Value | IncreaseInsulationRValueForRoofs | RubyMeasure
| argument | Insulation R-value (ft^2*h*R/Btu). | r_value | static | Double | 30
| argument | Increase in Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_increase_ip | static | Double | 0
| argument | One Time Retrofit Cost to Add Insulation to Construction ($/ft^2). | one_time_retrofit_cost_ip | static | Double | 0
| argument | Year to Incur One Time Retrofit Cost (whole years). | years_until_retrofit_cost | static | Integer | 0
FALSE | Inject OSM Geometry into an External IDF | InjectOsmGeometryIntoAnExternalIdf | EnergyPlusMeasure
| argument | Path to Source IDF File to Use. | source_idf_path | static | String
| argument | Merge Geometry From OpenStudio Model into Source IDF File? | merge_geometry_from_osm | static | Bool | TRUE
FALSE | Predicted Mean Vote | PredictedMeanVote | RubyMeasure
| argument | Enable ASHRAE 55 Comfort Warnings? | comfortWarnings | static | Bool | FALSE
| argument | Mean Radiant Temperature Calculation Type. | meanRadiantCalcType | static | Choice | ZoneAveraged | ¦ZoneAveraged,SurfaceWeighted¦
| argument | Choose a Work Efficiency Schedule. | workEfficiencySchedule | static | Choice
| argument | Choose a Clothing Insulation Schedule. | clothingSchedule | static | Choice | clothing_schedule_display_names[0] | ¦clothing_schedule_display_names[0]¦
| argument | Choose an Air Velocity Schedule. | airVelocitySchedule | static | Choice | airVelocity_schedule_display_names[0] | ¦airVelocity_schedule_display_names[0]¦
FALSE | Reduce Electric Equipment Loads by Percentage | ReduceElectricEquipmentLoadsByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Electric Equipment Power Reduction (%). | elecequip_power_reduction_percent | static | Double | 30
| argument | Increase in Material and Installation Cost for Electric Equipment per Floor Area (%). | material_and_installation_cost | static | Double | 0
| argument | Increase in Demolition Costs for Electric Equipment per Floor Area (%). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 15
| argument | Increase O & M Costs for Electric Equipment per Floor Area (%). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Lighting Loads by Percentage | ReduceLightingLoadsByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Lighting Power Reduction (%). | lighting_power_reduction_percent | static | Double | 30
| argument | Increase in Material and Installation Cost for Lighting per Floor Area (%). | material_and_installation_cost | static | Double | 0
| argument | Increase in Demolition Costs for Lighting per Floor Area (%). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 15
| argument | Increase O & M Costs for Lighting per Floor Area (%). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Night Time Electric Equipment Loads | ReduceNightTimeElectricEquipmentLoads | RubyMeasure
| argument | Pick an Electric Equipment Definition(schedules using this will be altered) | elec_load_def | static | Choice
| argument | Fractional Value for Night Time Load. | fraction_value | static | Double | 0.1
| argument | Apply Schedule Changes to Weekday and Default Profiles? | apply_weekday | static | Bool | TRUE
| argument | Weekday/Default Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_weekday | static | Double | 18
| argument | Weekday/Default Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_weekday | static | Double | 9
| argument | Apply Schedule Changes to Saturdays? | apply_saturday | static | Bool | TRUE
| argument | Saturday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_saturday | static | Double | 18
| argument | Saturday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_saturday | static | Double | 9
| argument | Apply Schedule Changes to Sundays? | apply_sunday | static | Bool | TRUE
| argument | Sunday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_sunday | static | Double | 18
| argument | Sunday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_sunday | static | Double | 9
| argument | Material and Installation Costs per Electric Equipment Quantity ($). | material_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs Costs per Electric Equipment Quantity ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Night Time Lighting Loads | ReduceNightTimeLightingLoads | RubyMeasure
| argument | Pick a Lighting Definition From the Model (schedules using this will be altered) | lights_def | static | Choice
| argument | Fractional Value for Night Time Load | fraction_value | static | Double | 0.1
| argument | Apply Schedule Changes to Weekday and Default Profiles? | apply_weekday | static | Bool | TRUE
| argument | Weekday/Default Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_weekday | static | Double | 18
| argument | Weekday/Default Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_weekday | static | Double | 9
| argument | Apply schedule changes to Saturdays? | apply_saturday | static | Bool | TRUE
| argument | Saturday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_saturday | static | Double | 18
| argument | Saturday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_saturday | static | Double | 9
| argument | Apply Schedule Changes to Sundays? | apply_sunday | static | Bool | TRUE
| argument | Sunday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_sunday | static | Double | 18
| argument | Sunday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_sunday | static | Double | 9
| argument | Material and Installation Costs per Light Quantity ($). | material_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs Costs per Light Quantity ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | ReduceSpaceInfiltrationByPercentage | ReduceSpaceInfiltrationByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Space Infiltration Power Reduction (%). | space_infiltration_reduction_percent | static | Double | 30
| argument | Increase in Material and Installation Costs for Building per Affected Floor Area ($/ft^2). | material_and_installation_cost | static | Double | 0
| argument | O & M Costs for Construction per Affected Floor Area ($/ft^2). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Ventilation By Percentage | ReduceVentilationByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Design Specification Outdoor Air Reduction (%). | design_spec_outdoor_air_reduction_percent | static | Double | 30
FALSE | RemoveUnusedDefaultProfiles | RemoveUnusedDefaultProfiles | RubyMeasure
FALSE | Rename Space Surfaces Based on Parent Space and Orientation | RenameSpaceSurfacesBasedonParentSpaceandOrientation | RubyMeasure
FALSE | Replace Exterior Window Constructions with a Different Construction from the Model | ReplaceExteriorWindowConstruction | RubyMeasure
| argument | Pick a Window Construction From the Model to Replace Existing Window Constructions. | construction | static | Choice
| argument | Change Fixed Windows? | change_fixed_windows | static | Bool | TRUE
| argument | Change Operable Windows? | change_operable_windows | static | Bool | TRUE
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Rotate Building Relative to Current Orientation | RotateBuilding | RubyMeasure
| argument | Number of Degrees to Rotate Building (positive value is clockwise). | relative_building_rotation | static | Double | 90
FALSE | Set COP for Two Speed DX Cooling Units | SetCOPforTwoSpeedDXCoolingUnits | RubyMeasure
| argument | Choose an Air Loop with a two speed DX Cooling Unit to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Rated High Speed COP | cop_high | static | Double | 4
| argument | Rated Low Speed COP | cop_low | static | Double | 4
| argument | Remove Baseline Costs From Effected Cooling Coil DX Two Speed Units? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs per Cooling Coil DX Two Speed Unit ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Cooling Coil DX Two Speed Unit ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Cooling Coil DX Two Speed Unit ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set EnergyPlus Light objects LPD | SetEnergyPlusLightObjectsLPD | EnergyPlusMeasure
| argument | Lighting Power Density (W/m^2) | lpd | static | Double | 10.76
FALSE | Set Ext Wall To Ground Boundary Condition By Story | SetExtWallToGroundBoundaryConditionByStory | RubyMeasure
| argument | Choose a Story to Change Wall Boundary Conditions For. | storyBasement | static | Choice
FALSE | Set Interior Walls to Adiabatic | SetInteriorWallsAndFloorsToAdiabatic | RubyMeasure
| argument | Select New Construction. | construction | static | Choice
FALSE | Set Interior Walls to Selected Construction | SetInteriorWallsToSelectedConstruction | RubyMeasure
| argument | Select new material: | construction | static | Choice
FALSE | Set Lifecycle Cost Parameters | SetLifecycleCostParameters | RubyMeasure
| argument | Set the Length of the Study Period (years). | study_period | static | Integer | 25
FALSE | Set Lighting Loads by LPD | SetLightingLoadsByLPD | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Lighting Power Density (W/ft^2) | lpd | static | Double | 1
| argument | Material and Installation Costs for Lights per Floor Area ($/ft^2). | material_cost | static | Double | 0
| argument | Demolition Costs for Lights per Floor Area ($/ft^2). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Lights per Floor Area ($/ft^2). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set Space Infiltration by Exterior Surface Area | SetSpaceInfiltrationByExteriorSurfaceArea | RubyMeasure
| argument | Space Infiltration Flow per Exterior Envelope Surface Area (cfm/ft^2).) #(ft^3/min)/(ft^2) = (ft/min | infiltration_ip | static | Double | 0.05
| argument | Increase in Material and Installation Costs for Building per Exterior Envelope Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set Window to Wall Ratio by Facade | SetWindowToWallRatioByFacade | RubyMeasure
| argument | Window to Wall Ratio (fraction). | wwr | static | Double | 0.4
| argument | Sill Height (in). | sillHeight | static | Double | 30
| argument | Cardinal Direction. | facade | static | Choice | South | ¦North,East,South,West¦
FALSE | Shift Schedule Profile Time | ShiftScheduleProfileTime | RubyMeasure
| argument | Choose a Schedule to Shift the Time For. | schedule | static | Choice | *All Ruleset Schedules* | ¦*All Ruleset Schedules*¦
| argument | Shift Schedule Profiles Forward (24hr, use decimal for sub hour). | shift_value | static | Double | 1
FALSE | Swap Lights Definition | SwapLightsDefinition | RubyMeasure
| argument | Choose the Lights Definition you Want to Replace. | old_lights_def | static | Choice
| argument | Choose the Lights Definition to Use in Place of Removed Definition. | new_lights_def | static | Choice
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
FALSE | Xcel EDA Reporting and QAQC | XcelEDAReportingandQAQC | ReportingMeasure
FALSE | Xcel EDA Tariff Selection and Model Setup | XcelEDATariffSelectionandModelSetup | EnergyPlusMeasure
| argument | Select an Electricity Tariff. | elec_tar | static | Choice | Secondary General | ¦Residential General,Commercial,Primary General,Secondary General Low Load Factor,Secondary General,Secondary Photovoltaic Time-of-Use,Transmission General,Non-Xcel Commercial,Non-Xcel Primary General,Non-Xcel Secondary General Low Load Factor,Non-Xcel Secondary General,Non-Xcel Transmission General¦
| argument | Select a Gas Tariff. | gas_tar | static | Choice | Large CG | ¦Residential Gas,Small CG,Large CG,Interruptible Industrial G,Non-Xcel Gas Firm,Non-Xcel Gas Interruptible¦
FALSE | Set Boiler Thermal Efficiency | SetBoilerThermalEfficiency | RubyMeasure
| argument | Apply the measure to | boiler_widget | static | Choice | boiler_display_names[0] | ¦0,boiler_display_names[0]¦
| argument | Option 1, set boiler nominal thermal efficiency to a user defined value | input_option_manual | static | Bool | FALSE
| argument | Boiler nominal thermal efficiency (between 0 and 1) | boiler_thermal_efficiency | static | Double | 0.8
| argument | Option 2, set boiler nominal thermal efficiency based on ASHRAE Standard 90.1 requirement | input_option_standard | static | Bool | FALSE
| argument | Boiler nominal capacity [W] | nominal_capacity | static | Double
| argument | Fuel type | fuel_type_widget | static | Choice | fuel_type_display_names[0] | ¦0,1,2,fuel_type_display_names[0]¦
| argument | ASHRAE Standards 90.1 | standards_widget | static | Choice | standards_display_names[0] | ¦0,1,2,3,4,standards_display_names[0]¦
FALSE | Set Water Heater Efficiency, Heat Loss, and Peak Water Flow Rate | SetWaterHeaterEfficiencyHeatLossandPeakWaterFlowRate | RubyMeasure
| argument | Apply the measure to | waterheater_widget | static | Choice | waterheater_display_names[0] | ¦0,waterheater_display_names[0]¦
| argument | Fuel type | heater_fuel_type_widget | static | Choice | heater_fuel_type_display_names[0] | ¦heater_fuel_type_display_names[0]¦
| argument | Thermal efficiency [between 0 and 1] | heater_thermal_efficiency | static | Double | 0.8
| argument | Loss coefficient to ambient temperature [W/K] (optional input, baseline value will be used if empty) | onoff_cycle_loss_coefficient_to_ambient_temperature | static | Double | 0
| argument | Peak water use flow rate [m3/s] (optional input, baseline value will be used if empty) | peak_use_flow_rate | static | Double
FALSE | SetChillerCOP | SetChillerCOP | RubyMeasure
| argument | Apply the measure to | chiller_widget | static | Choice | *All chillers* | ¦*All chillers*¦
| argument | Chiller Rated COP (more than 0) | chiller_thermal_efficiency | static | Double | 3 |  | 2.5 | 5.5 | 4 | 0.5 | triangle_uncertain
FALSE | Set Minimum VAV Terminal Flow Fraction | SetMinimumVAVTerminalFlowFraction | RubyMeasure
| argument | Minimum VAV Terminal Flow Fraction (%) | min_vav_frac | static | Double | 30
FALSE | Add Cost per Floor Area to Building | AddCostPerFloorAreaToBuilding | RubyMeasure
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Name for Life Cycle Cost Object. | lcc_name | static | String | Building - Life Cycle Costs
| argument | Material and Installation Costs for the Building per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for the Builiding per Floor Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set Heating and Cooling Sizing Factors | SetHeatingandCoolingSizingFactors | RubyMeasure
| argument | Heating Sizing Factor (eg 1.25 = 125% of required heating capacity. | htg_sz_factor | static | Double | 1.25
| argument | Coolinig Sizing Factor (eg 1.15 = 115% of required cooling capacity. | clg_sz_factor | static | Double | 1.15
FALSE | SetChillerCOP | SetChillerCOP | RubyMeasure
| argument | Apply the measure to | chiller_widget | static | Choice | *All chillers* | ¦*All chillers*¦
| variable | Chiller Rated COP (more than 0) | chiller_thermal_efficiency | lhs | Double | 3 |  | 2.5 | 5.5 | 4 | 0.5 | triangle_uncertain
FALSE | Set Chilled Water Loop Temperature | SetChilledWaterLoopTemperature | RubyMeasure
| argument | Desired chilled water setpoint (F) | cw_temp_f | static | Double | 45
FALSE | Set Hot Water Loop Temperature | SetHotWaterLoopTemperature | RubyMeasure
| argument | Desired hot water setpoint (F) | hw_temp_f | static | Double | 140

## Lookups
Instances | Number of Cores | Cost | Storage | Notes
m3.medium | 1 Cores | $0.07/hour | 4 GB | Use only for cluster configuration testing
m3.large | 2 Cores | $0.14/hour | 32 GB | Recommended for Server
m3.xlarge | 4 Cores | $0.28/hour | 40 GB | Recommended for Server
m3.2xlarge | 8 Cores | $0.56/hour | 80 GB | Recommended for Server
c3.large | 2 Cores | $0.11/hour | 16 GB | Can be used as worker
c3.xlarge | 4 Cores | $0.21/hour | 40 GB | Can be used as worker
c3.2xlarge | 8 Cores | $0.42/hour | 80 GB | Recommended for worker
c3.4xlarge | 16 Cores | $0.84/hour | 160 GB | Recommended for worker
c3.8xlarge | 32 Cores | $1.68/hour | 320 GB | Recommended for worker
SensitivityType |  | TrueFalse |  | Workflow |  | Simulation
individual_variables |  | TRUE |  | run_openstudio_workflow.rb |  | simulate_data_point.rb
all_variables |  | FALSE |  | run_openstudio_workflow_monthly.rb
AnalysisType |  | batch_run |  |  | lhs |  |  | Optim |  |  | Rgenoud |  |  | Nsga |  |  | preflight | doe |  |  | single_run | repeat_run |  |  | baseline_perturbation
batch_run |  |  |  |  | Sample Method | individual_variables | individual_variables / all_variables | epsilonGradient | 0.01 | epsilon in gradient calculation | popSize | 30 | Size of initial population | Number of Samples | 30 | Size of initial population |  | Experiment Type | full_factorial | full_factorial |  | Number of Runs | 30 | positive integer (if individual, total simulations is this times each variable) | in_measure_combinations | TRUE | (TRUE/FALSE) Run full factorial search over in-measure variable combinations
lhs |  |  |  |  | Number of Samples | 30 | positive integer (if individual, total simulations is this times each variable) | pgtol | 0.01 | tolerance on the projected gradient | Generations | 5 | Number of generations | Generations | 3 | Number of generations |  | Number of Samples | 2 | positive integer (this discretizes a continous variable) |  |  |  |  | include_baseline_in_combinations | TRUE | (TRUE/FALSE) If in_measure_combinations are TRUE, sets if static values be included in combinations
optim | [7 empty] | factr | 45036000000000 | Tolerance on delta_F | waitGenerations | 2 | If no improvement in waitGenerations of generations, then exit | cprob | 0.85 | Crossover probability [0,1]
rgenoud | [7 empty] | maxit | 100 | Maximum number of iterations | bfgsburnin | 2 | The number of generations which are run before the BFGS is ﬁrst used | XoverDistIdx | 5 | Crossover Distribution Index (large values give higher probabilities of offspring close to parent)
nsga_nrel | [7 empty] | normType | minkowski |  | gradientcheck | 1 | 0 false / 1 true | MuDistIdx | 5 | Mutation Distribution Index (large values give higher probabilities of offspring close to parent)
preflight | [7 empty] | pPower | 2 | Lp norm power | solutionTolerance | 0.01 | Numbers within solutionTolerance are considered equal | mprob | 0.8 | Mutation probability [0,1]
doe | [7 empty] | Exit On Guideline14 | 0 | 0 false / 1 true (for use with calibration report) | epsilonGradient | 0.01 | epsilon in gradient calculation | toursize | 2 | Tournament Size
single_run | [10 empty] | pgtol | 0.01 | tolerance on the projected gradient | normType | minkowski
repeat_run | [10 empty] | factr | 45036000000000 | Tolerance on delta_F | pPower | 2 | Lp norm power
baseline_perturbation | [10 empty] | maxit | 100 | Maximum number of iterations | Exit On Guideline14 | 0 | 0 false / 1 true (for use with calibration report)
[11 empty] | normType | minkowski
[11 empty] | pPower | 2 | Lp norm power
[11 empty] | Exit On Guideline14 | 0 | 0 false / 1 true (for use with calibration report)
[11 empty] | balance | 1 | 0 false / 1 true (load balancing)